## Summary
ILEA's current daily maintenance log is below.

## Detail
Dedicated Outdoor Air Unit (Heating Water/Chilled Water)
Tag Name | Area Served | Max Dimensions |  |  | Supply Fan | [10 empty] | EXHAUST FAN | [9 empty] | HEATING COIL - Water | [6 empty] | COOLING COIL - Chilled Water
[12 empty] | Disconnect |  | Controller/Starter | [7 empty] | Disconnect |  | Controller/Starter |  | EAT °F DB | MIN. LAT °F (NOTE 1) | EWT | GPM | Total MBH | MAX. A.P.D. IN. W.C. | WPD | EAT °F DB | EAT °F WB | MAX. LAT °F DB (NOTE 1) | LAT °F WB | COOLING COIL EWT | COOLING COIL LWT | COOLING COIL GPM | TOTAL MBH | MAX. A.P.D. IN. W.C. | COOLING COIL WPD
|  | Length | Width | Height | CFM Capacity | Balance CFM | EXT S>P | Type | RPM (Note D) | BHP (Note E) | MHP (Note D) | By | Type | By | Type | CFM Capacity | Balance CFM | EXT. S.P | Type | RPM | BHP | By | Type | By | Type
DOAS-1 | 1968 BUILDING | 206" | 56" | 84" | 3000 | 2470 | 0.55 | AF | 1750 | 2.4 | 3 | MFR | NF | MFR | VFD | 3000 | 2470 | 0.5 | AF | 3500 | 2.3 | MFR | NF | MFR | VFD | 45.7 | 70 | 150 | 18.4 | 266 | 0.2 | 2.4 | 81.5 | 68.7 | 54.3 | 53.9 | 42 °F | 56 °F | 19.8 GPM | 140 | 0.3 | 3 FT
Dedicated Outdoor Air Unit (Heating Water/DX)
Tag Name | Area Served | Max Dimensions |  |  | Supply Fan | [10 empty] | EXHAUST FAN | [9 empty] | HEATING COIL - Water | [7 empty] | HOT GAS REHEAT |  |  | COOLING COIL-DX
[12 empty] | Disconnect |  | Controller/Starter | [7 empty] | Disconnect |  | Controller/Starter |  | EAT °F DB | EAT °F WB | MIN. LAT °F (NOTE 1) | LWT | GPM | Total MBH | MAX. A.P.D. IN. W.C. | WPD | EAT | LAT | CAPACITY MBH | Refrigerant Type | EAT °F DB | EAT °F WB | MAX. LAT °F DB (NOTE 1) | LAT °F WB | TOTAL MBH | MAX. A.P.D. IN. W.C.
|  | Length | Width | Height | CFM Capacity | Balance CFM | EXT S>P | Type | RPM (Note D) | BHP (Note E) | MHP (Note D) | By | Type | By | Type | CFM Capacity | Balance CFM | EXT. S.P | Type | RPM | BHP | By | Type | By | Type
DOAS-2 | Dorm Wing | 205.9" | 76.5" | 70.5" | 3600 | 3045 | 0.5 | AF | 1655 | 2.9 | 5 | MFR | NF | MFR | VFD | 3600 | 3045 | 0.75 | AF | 1494 | 1.3 | MFR | NF | MFR | ECM | -10 | -10 | 70 | 120 | 34.4 | 494 | 0.2 | 3.4 | 54.4 | 70 | 60.889 | R410A | 84.4 | 70.5 | 54.4 | 54.4 | 187 | 0.2
DOAS-3 | Classrooms | 132.7" | 96.5" | 56.8" | 2300 | 1700 | 0.75 | AF | 1662 | 0.9 | 4 | MFR | NF | MFR | ECM | 2300 | 1700 | 0.95 | AF | 1617 | 0.9 | MFR | NF | MFR | ECM | -10 | -10 | 70 | 120 | 16.4 | 232 | 0.2 | 6.24 | 52.1 | 70 | 44.673 | R410A | 81.2 | 68.1 | 52.1 | 51.8 | 115 | 0.1
DOAS-4 | Dining | 103" | 87" | 40.8" | 1350 | 1350 | 0.75 | AF | 2050 | 1 | 2.3 | MFR | NF | MFR | ECM | 1350 | 465 | 0.9 | AF | 2290 | 0.7 | MFR | NF | MFR | ECM | -10 | -10 | 70 | 120 | 8.2 | 116 | 0.2 | 3.17 | 52.3 | 70 | 25.907 | R410A | 81.9 | 68.8 | 52.3 | 52.3 | 69 | 0.3
DOAS-5 | Support Space | 132.7" | 96.5" | 56.8" | 2000 | 1740 | 0.5 | AF | 1444 | 0.6 | 4 | MFR | NF | MFR | ECM | 2000 | 1420 | 0.5 | AF | 1753 | 0.6 | MFR | NF | MFR | ECM | -10 | -10 | 70 | 120 | 14.7 | 209 | 0.1 | 5.1 | 53.6 | 70 | 35.523 | R410A | 81.2 | 68.1 | 53.6 | 53.6 | 90 | 0.1
Dedicated Outdoor Air Units
Tag name | Energy Recover wheel | [17 empty] | Filter |  |  | Roof Curb | Vibration Isolation |  | ELECTRICAL | [7 empty] | Manufacturer | Model | Notes
| Type |  | Outdoor Air | [9 empty] | Relief Air | [5 empty] | Type | Velocity | Pressure Drop Clean (IN. W.G.) |  | Type | DEFL. |  |  |  |  | Disconnect |  | Controller/Starter
|  | Winter Effectiveness | CFM | Summer |  |  |  | Winter |  |  |  |  | CFM | Summer |  | Winter
|  |  |  | EAT DB | EAT WB | LAT DB | LATWB | EAT DB | EAT WB | LAT DB | LAT WB | APD |  | EAT DB | EAT WB | EAT DB | EAT WB | APD | [6 empty] | Voltage | Phases | FLA | MCA | By | Type | By | Type
DOAS-1 | Wheel | 72.07 | 3000 | 95 | 78 | 81.5 | 68.7 | -10 | -10 | 45.7 | 36 | 1.04 | 3000 | 75 | 62 | 70 | 50 | 1.02 | Pleated | 253 | 0.09 | N/A | M3 | 0.75 | 208 | 3 | 39 | 45 | MFR | NF | MFR | VFD | Dalkin Applied | CAH
DOAS-2 | Wheel | 74 | 3600 | 95 | 78 | 79.5 | 67.4 | -10 | -10 | 49.7 | 38.3 | 0.47 | 3600 | 75 | 63 | 70 | 50 | 0.47 | Pleated | 133 | 0.04 | MFR | SAC | 0.75 | 208 | 3 | 79 | 91 | MFR | NF | MFR | VFD | Dalkin Applied | DPS-016
DOAS-3 | Wheel | 72 | 2300 | 95 | 78 | 80.1 | 67.2 | -10 | -10 | 47.3 | 36.8 | 0.52 | 2300 | 75 | 62 | 70 | 50 | 0.52 | Pleated | 128 | 0.03 | MFR | SAC | 0.75 | 208 | 3 | 49 | 54 | MFR | NF | MFR | VFD | Dalkin Applied | DPS-010
DOAS-4 | Wheel | 63 | 1350 | 95 | 78 | 81.9 | 68.8 | -10 | -10 | 39.4 | 31.6 | 0.99 | 1350 | 75 | 62 | 70 | 50 | 0.99 | Pleated | 190 | 0.06 | MFR | SAC | 0.75 | 208 | 3 | 25 | 29 | MFR | NF | MFR | VFD | Dalkin Applied | DPS-006
DOAS-5 | Wheel | 75 | 2000 | 95 | 78 | 79.6 | 68.8 | -10 | -10 | 49.6 | 38.2 | 0.45 | 2000 | 75 | 62 | 70 | 50 | 0.45 | Pleated | 111 | 0.02 | MFR | SAC | 0.75 | 208 | 3 | 38 | 41 | MFR | NF | MFR | VFD | Dalkin Applied | DPS-010
Fan Schedule
Tag Name | Area Served | CFM | S.P. IN. W.C | Wheel Dia. Inches | Fan RPM | Drive Type | Max. AMCA Sones | Backdraft Damper Type | Curb Type | Vibration Isolation |  | Electrical | [8 empty] | Manufacturer | Model | Notes
[10 empty] | Type | DEFL. | BHP | MHP | Voltage | Phases | Disconnect |  | Controller/Starter
[16 empty] | By | Type | By | Type | SCCR
EF-3 | MECH ROOM | 900 | 0.4 | 11 | 1109 | Belt | 9.1 | Gravity | Inline | H3 | .75" | 0.19 | 0.25 | 208 | 1 | MFR | NF | MFR | FV | 10000 | Greenheck | BSQ-90
Motor Operated Damper Schedule
Tag Name | Area Served | Size |  | CFM | Blade Configureation | Blade Orientation | Insulated | Actuator Type | Actuator Style | Power Failure Position | Positive Position Feedback Requered
|  | Width | Height
MOD-1 | BCU-1 | 24 | 12 | 900 | Opposed | Horizontal | Yes | Electric | Two Position | Normally Open | Yes
Air Cooled Chiller Schedule
Tag Name | Area Servied | Max Dimensions |  |  | Refrigerant | AMBIENT TEMP °F | MIN. Operating Ambient Temp °F | Capacity/ Performance | [6 empty] | Evaporator Perfomance |  |  |  |  | Vibration Isolation |  | MAXIMUM ALLOWABLE SOUND POWER IN DB RE 10¯¹² WATTS OCTAVE BAND CENTER FREQUENCY | [6 empty] | Electrical | [9 empty] | Manufacturer | Model
[8 empty] | Design Tons | Stages of Unloading | MIN. EER AT % Load (Based on Air and Water Conditions as Listed.) |  |  |  | NPLV | [14 empty] | Voltage | Phases | FLA | MCA | MOCP AMPS | Disconnect |  | Controller/Starter
|  | Length | Width | Height | [5 empty] | 100 | 75 | 50 | 30 |  | EWT °F | LWT °F | GPM | Max Pressure Drop (FT. W.G.) | Fouling Factor | Type | DEFL. | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | [5 empty] | By | Type | By | Type | SCCR
CHR-1 | Building | 192.1" | 88" | 98.6" | R410A | 95 °F | 0 °F | 124.1 | 8 | 9.79 | 13.29 | 16.15 | 17.99 | 15.44 | 56 °F | 42 °F | 211.7 | 4.5 | 0.0001 | M2 | 1/4" | 94 | 97 | 93 | 93 | 91 | 85 | 85 | 208 V | 3 | 455 A | 569A | 700A | MFR | F | MFR | FV | 5000 | Dalkin Applied | AGZ130E
Boiler Schedule - Hot Water
Tag Name | Max. Dimensions |  |  | Fuel | Max. Inlet Fuel Pressure (IN. W.C.) | Turndown Ratio | Input BTUH/HR | EWT °F | LWT °F | Operationg Pressure PSI | Electrical | [5 empty] | Manufacturer | Model
[11 empty] | Voltage | Phases | Disconnect |  | Controller/Starter
| Length | Width | Height | [9 empty] | BY | Type | BY | SCCR
BLR-1 | 84 5/8" | 30" | 80" | Natural Gas | 14 | 10:01 | 2500000 | 2420000 | 120 | 150 | 208 | 3 | EC | NF | MFR | 10000 | Fulton | EDR +2500
BLR-2 | 84 5/8" | 30" | 80" | Natural Gas | 14 | 10:01 | 2500000 | 2420000 | 120 | 150 | 208 | 3 | EC | NF | MFR | 10000 | Fulton | EDR +2500
Pump Schedule
Tag Name | Area Served | GPM | Pump FT. Head at Design | Minimum Pump Efficiency | Inlet Size | Impeller Sizer | Vibration Isolation |  | Electrical | [8 empty] | Manufacturer | Model
[7 empty] | Type | Defl. | HP | BHP | RPM | Voltage | Phases | Disconnect |  | Controller/Starter
[14 empty] | By | Type | By | Type
CWP-1 | Building | 215 | 90 | 72 | 3" | 10.125 | M3 | 3/4" | 10 | 7.02 | 1800 | 208 | 3 | EC | NF | EC | VFD | B&G | 1510 2EB
CWP-2 (F) | Building | 215 | 90 | 72 | 3" | 10.125 | M3 | 3/4" | 10 | 7.02 | 1800 | 208 | 3 | EC | NF | EC | VFD | B&G | 1510 2EB
HWCP-1 | DOAS-1 | 18.4 | 18.5 | 56.1 | 1 1/4" | 4.375 | H2 | 3/4" | 0.33 | 0.156 | 1725 | 120 | 1 | EC | NF | EC | ECM | B&G | e-90 1.25 AAB
HWCP-2 | DOAS-2 | 34.4 | 16 | 65.1 | 1 1/4" | 4.375 | H2 | 3/4" | 0.33 | 0.224 | 1725 | 120 | 1 | EC | NF | EC | ECM | B&G | e-90 1.25 AAB
HWCP-3 | DOAS-3 | 16.4 | 19 | 52.9 | 1 1/4" | 4.5 | H2 | 1 1/2" | 0.5 | 0.161 | 1725 | 120 | 1 | EC | NF | EC | ECM | B&G | e-90 1.25 AAB
HWCP-4 | DOAS-4 | 8.2 | 16 | 40.3 | 1" | 4.125 | H2 | 1 1/2" | 0.25 | 0.0805 | 1725 | 120 | 1 | EC | NF | EC | ECM | B&G | e-90 1AAB
HWCP-5 | DOAS-5 | 14.7 | 18 | 51.7 | 1 1/4" | 4.375 | H2 | 1 1/2" | 0.33 | 0.139 | 1725 | 120 | 1 | EC | NF | EC | ECM | B&G | e-90 1.25 AAB
HWCP-6 | BCU-1 | 7.5 | 19 | 38.1 | 1" | 4.5 | H2 | 3/4" | 0.33 | 0.0951 | 1725 | 120 | 1 | EC | NF | EC | ECM | B&G | e-90 1AAB
HWP-1 | Building | 175 | 70 | 74 | 2 1/2" | 8.75 | M3 | 3/4" | 7.5 | 4.2 | 1800 | 208 | 3 | EC | NF | EC | VFD | B&G | 1510 2BD
HWP-2 | Building | 175 | 70 | 74 | 2 1/2" | 8.75 | M3 | 3/4" | 7.5 | 4.2 | 1800 | 208 | 3 | EC | NF | EC | VFD | B&G | 1510 2BD
Glycol Feed System
Tag Name | Area Served | Tank Volume | Sytem Fill Pressure | Pump Head PSI | GPM | Electrical | [5 empty] | Manufacturer | Model
[6 empty] | MHP | Voltage | Phases | Disconnect By | Controller/Starter
[10 empty] | By | SCCR
GFS-1 | Building | 50 | 26 | 30 | 1.8 | 0.33 | 120 | 1 | MFR | MFR | 10000 | Wessels | GMP- 13050
Blower Coil Unit Schedule
Tag Name | Area Served | Configuration | CFM | EXT. S.P. IN W.C. | Heating Coil | [6 empty] | Electrical | [7 empty] | Manufacturer | Model
[5 empty] | EAT |  | Total MBH | GPM | EWT °F | LWT °F | W.P.D. FT. HD | HP | RPM |  |  | Disconnect |  | Controller/Starter
[5 empty] | DB °F | WB °F | [7 empty] | Voltage | Phases | BY | Type | By | SCCR
BCU-1 | Chiller Room | Horizontal | 900 | 0.8 | -10 | 0.1 | 105.177 | 7.5 | 150 | 120 | 6.4 | 1 | 1333 | 208 | 1 | EC | NF | MFR | 5000 | IEC | HDY08
Cabinet Heater Schedule - Hot Water
Tag Name | Area Served | Max. Dimensions |  |  | Configuration | Nominal CFM | MBH | GPM | EWT °F | LWT °F | MAX W.P.D. FT. HD | Control Type | Cabinet |  |  | Electrical | [6 empty] | Manufacturer | Model
[13 empty] | Height | Width | Depth | FanHP | Voltage | Phases | Disconnect |  | Controller/ Starter
|  | Length | Width | Height | [14 empty] | By | Type | By | SCCR
CAB-1 | Vestibule | 29" | 9.25" | 25" | Vertical Recessed | 305 | 14.9 | 1.1 | 150 | 120 | 3.5 | FV | 30" | 44" | 0" | 0.033 | 208 | 1 | EC | NF | MFR | 2000 | IEC | FHY03
CAB-2 | Vestibule | 29" | 9.25" | 25" | Vertical Recessed | 305 | 14.9 | 1.1 | 150 | 120 | 3.5 | FV | 30" | 44" | 0" | 0.033 | 208 | 1 | EC | NF | MFR | 2000 | IEC | FHY03
CAB-3 | Stair 129 | 23.5" | 42" | 11" | Suspended Cabinet | 300 | 13.2 | 0.9 | 150 | 120 | 2.8 | FV | 11" | 24" | 42" | 0.033 | 208 | 1 | EC | NF | MFR | 2000 | IEC | CXB03
CAB-4 | Stair 123 | 51" | 9" | 25" | Floor Mounted Flat Top | 400 | 20 | 1.4 | 150 | 120 | 1.6 | FV | 25" | 51" | 9" | 0.083 | 208 | 1 | EC | NF | MFR | 2000 | IEC | FXC04
Split System Unit Schedule
Tag Name | Area Served | Max. Dimensions (Indoor Unit) |  |  | Indoor Unit | [7 empty] | Outdoor Unit | [5 empty] | Electrical
[5 empty] | CFM | MCA | MOCP AMPS | Voltage | Phase | Cooling MBH | Manufacturer | Model | SEER | MCA | MOCP | Voltage | Phases | Model | Disconnect |  | Controller/ Starter
|  | Length | Width | Height | [14 empty] | By | Type | By | SCCR
SS-1 | Elevator Equipment Room | 46 1/16" | 11 5/8" | 14 3/8" | 775 | 1 | 15 | 208 | 1 | 24 | Mitsubishi | PKA-A24FA | 17 | 18 | 30 | 208 | 1 | Mitsubishi | MFR | NF | MFR | 42000
SS-2 | Electrical 104-EC | 46 1/16" | 11 5/8" | 14 3/8" | 775 | 1 | 15 | 208 | 1 | 24 | Mitsubishi | PKA-A24FA | 17 | 18 | 30 | 208 | 1 | Mitsubishi | MFR | NF | MFR | 42000
SS-3 | IT 105-IT | 35 3/8" | 9 13/16" | 11 5/8" | 425 | 1 | 15 | 208 | 1 | 12 | Mitsubishi | PKA-A12GA | 15.2 | 13 | 15 | 208 | 1 | Mitsubishi | MFR | NF | MFR | 22000
SS-4 | IT 205-IT | 35 3/8" | 9 13/16" | 11 5/8" | 425 | 1 | 15 | 208 | 1 | 12 | Mitsubishi | PKA-A12GA | 15.2 | 13 | 15 | 208 | 1 | Mitsubishi | MFR | NF | MFR | 10000
FAN COIL UNIT SCHEDULE - HYDRONIC
TAG NAME | MAX. DIMENSIONS |  |  | CFM | EXT. S.P. IN W.C. | EAT |  | COOLING COIL (NOTES 5 & 6) | [5 empty] | HEATING COIL (NOTES 5 & 6) |  |  |  |  | ELECTRICAL | [6 empty] | SENSOR TYPE (NOTE H) | MANUFACTURER | MODEL
| LENGTH | WIDTH | HEIGHT |  |  | DB °F | WB °F | TOTAL MBH | SENSIBLE MBH | GPM | EWT °F | LWT °F | W.P.D. FT. HD | TOTAL MBH | GPM | EWT °F | LWT °F | W.P.D. FT. HD | HP | VOLTAGE | PHASES | DISCONNECT |  | CONTROLLER/ STARTER
[22 empty] | BY (NOTE A) | TYPE (NOTE B) | TYPE (NOTE A) | SCCR
FCU-103 | 20" | 31.25" | 10.5" | 395 | 0.4 | 75 | 63 | 4.3 | 4 | 1.6 | 42 | 56 | 9.9 | 4.9 | 0.5 | 150 | 120 | 0.4 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY04B6
FCU-107A | 24" | 24" | 88" | 1250 | 0.4 | 75 | 63 | 20.3 | 19.1 | 5.4 | 42 | 56 | 6.5 | 24.1 | 2.4 | 150 | 120 | 2.4 | 0.25 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | MPY12B6
FCU-107B | 24" | 24" | 88" | 1250 | 0.4 | 75 | 63 | 20.3 | 19.1 | 5.4 | 42 | 56 | 6.5 | 24.1 | 2.4 | 150 | 120 | 2.4 | 0.25 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | MPY12B6
FCU-107C | 24" | 24" | 88" | 1250 | 0.4 | 75 | 63 | 25.6 | 21.4 | 5.4 | 42 | 56 | 6.5 | 11.6 | 2.4 | 150 | 120 | 2.4 | 0.25 | 208 | 1 | MFR | NF | MFR | 2000 | S4 | IEC | MPY12B6
FCU-107D | 24" | 24" | 88" | 1250 | 0.4 | 75 | 63 | 25.6 | 21.4 | 5.4 | 42 | 56 | 6.5 | 11.6 | 2.4 | 150 | 120 | 2.4 | 0.25 | 208 | 1 | MFR | NF | MFR | 2000 | S4 | IEC | MPY12B6
FCU-108 | 32" | 36" | 18" | 780 | 0.4 | 75 | 63 | 10.5 | 9.5 | 2.2 | 42 | 56 | 0.8 | 11.1 | 1 | 150 | 120 | 2.2 | 0.13 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | HLY08B6
FCU-109 | 32" | 40" | 18" | 875 | 0.4 | 75 | 63 | 18.7 | 17.9 | 3 | 42 | 56 | 1.4 | 20.2 | 1.4 | 150 | 120 | 3.5 | 0.25 | 208 | 1 | MFR | NF | MFR | 2000 | S2 | IEC | HLY10B6
FCU-110 | 20" | 31.25" | 10.5" | 395 | 0.4 | 75 | 63 | 3.7 | 3.6 | 1.6 | 42 | 56 | 9.9 | 4 | 0.5 | 150 | 120 | 0.4 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S2 | IEC | CPY04B6
FCU-112A | 24" | 53" | 14" | 605 | 0.4 | 75 | 63 | 13.9 | 12.1 | 2.4 | 42 | 56 | 4.7 | 13.3 | 0.9 | 150 | 120 | 0.9 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S3 | IEC | CBY08B6
FCU-112B | 24" | 53" | 14" | 605 | 0.4 | 75 | 63 | 13.9 | 12.1 | 2.4 | 42 | 56 | 4.7 | 13.3 | 0.9 | 150 | 120 | 0.9 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S3 | IEC | CBY08B6
FCU-114A | 24" | 24" | 88" | 1250 | 0.4 | 75 | 63 | 32.2 | 23.2 | 5.4 | 42 | 56 | 6.5 | 18.7 | 2.4 | 150 | 120 | 2.4 | 0.25 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | MPY12B6
FCU-114B | 24" | 24" | 88" | 1250 | 0.4 | 75 | 63 | 32.2 | 23.2 | 5.4 | 42 | 56 | 6.5 | 18.7 | 2.4 | 150 | 120 | 2.4 | 0.25 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | MPY12B6
FCU-114C | 24" | 24" | 88" | 1250 | 0.4 | 75 | 63 | 32.2 | 23.2 | 5.4 | 42 | 56 | 6.5 | 18.7 | 2.4 | 150 | 120 | 2.4 | 0.25 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | MPY12B6
FCU-114D | 24" | 24" | 88" | 1250 | 0.4 | 75 | 63 | 32.2 | 23.2 | 5.4 | 42 | 56 | 6.5 | 18.7 | 2.4 | 150 | 120 | 2.4 | 0.25 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | MPY12B6
FCU-118 | 24" | 53" | 14" | 605 | 0.4 | 75 | 63 | 9.2 | 8.4 | 2.4 | 42 | 56 | 4.7 | 9.9 | 0.9 | 150 | 120 | 0.9 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CBY08B6
FCU-119A | 24" | 53" | 14" | 605 | 0.4 | 75 | 63 | 30 | 28.6 | 2.4 | 42 | 56 | 4.7 | 41.9 | 0.9 | 150 | 120 | 0.9 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CBY08B6
FCU-119B | 24" | 53" | 14" | 605 | 0.4 | 75 | 63 | 30 | 28.6 | 2.4 | 42 | 56 | 4.7 | 41.9 | 0.9 | 150 | 120 | 0.9 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CBY08B6
FCU-120 | 24" | 41" | 14" | 395 | 0.4 | 75 | 63 | 3.6 | 3.1 | 1.6 | 42 | 56 | 9.9 | 3.8 | 0.5 | 150 | 120 | 0.4 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CBY04B6
FCU-121 | 24" | 41" | 14" | 395 | 0.4 | 75 | 63 | 4.8 | 4.3 | 1.6 | 42 | 56 | 9.9 | 5.3 | 0.5 | 150 | 120 | 0.4 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CBY04B6
FCU-124 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 18.4 | 15.3 | 3 | 42 | 56 | 1.4 | 18.3 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-125A | 20" | 65.25" | 10.5" | 1020 | 0.4 | 75 | 63 | 24.2 | 17.4 | 3.7 | 42 | 56 | 2.2 | 21 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S3 | IEC | CPY12B6
FCU-125B | 20" | 65.25" | 10.5" | 1020 | 0.4 | 75 | 63 | 24.2 | 17.4 | 3.7 | 42 | 56 | 2.2 | 21 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S3 | IEC | CPY12B6
FCU-125C | 20" | 65.25" | 10.5" | 1020 | 0.4 | 75 | 63 | 24.2 | 17.4 | 3.7 | 42 | 56 | 2.2 | 21 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S3 | IEC | CPY12B6
FCU-130 | 31" | 32" | 18" | 610 | 0.4 | 75 | 63 | 6 | 5.3 | 1.6 | 42 | 56 | 0.4 | 6.6 | 0.7 | 150 | 120 | 1 | 0.1 | 208 | 1 | MFR | NF | MFR | 2000 | S2 | IEC | HLY06B6
FCU-133 | 32" | 40" | 18" | 875 | 0.4 | 75 | 63 | 18.6 | 17.4 | 3 | 42 | 56 | 1.4 | 19.1 | 1.4 | 150 | 120 | 3.5 | 0.25 | 208 | 1 | MFR | NF | MFR | 2000 | S2 | IEC | HLY10B6
FCU-202 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 20.6 | 19.6 | 3 | 42 | 56 | 1.4 | 20.5 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S4 | IEC | CPY10B6
FCU-203 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 18.2 | 15.2 | 3 | 42 | 56 | 1.4 | 11.7 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S3 | IEC | CPY10B6
FCU-204A | 24" | 53" | 14" | 605 | 0.4 | 75 | 63 | 9.8 | 9 | 2.4 | 42 | 56 | 4.7 | 10.7 | 0.9 | 150 | 120 | 0.9 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S3 | IEC | CBY08B6
FCU-204B | 24" | 53" | 14" | 605 | 0.4 | 75 | 63 | 6.9 | 6.1 | 2.4 | 42 | 56 | 4.7 | 7.2 | 0.9 | 150 | 120 | 0.9 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S3 | IEC | CBY08B6
FCU-204C | 24" | 53" | 14" | 605 | 0.4 | 75 | 63 | 9.8 | 9 | 2.4 | 42 | 56 | 4.7 | 10.7 | 0.9 | 150 | 120 | 0.9 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S3 | IEC | CBY08B6
FCU-206A | 20" | 31.25" | 10.5" | 395 | 0.4 | 75 | 63 | 15 | 14.6 | 1.6 | 42 | 56 | 9.9 | 12.2 | 0.5 | 150 | 120 | 0.4 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY04B6
FCU-206B | 20" | 31.25" | 10.5" | 395 | 0.4 | 75 | 63 | 15 | 14.6 | 1.6 | 42 | 56 | 9.9 | 12.2 | 0.5 | 150 | 120 | 0.4 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY04B6
FCU-207 | 20" | 31.25" | 10.5" | 395 | 0.4 | 75 | 63 | 2.6 | 2.2 | 1.6 | 42 | 56 | 9.9 | 0.8 | 0.5 | 150 | 120 | 0.4 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY04B6
FCU-209 | 20" | 31.25" | 10.5" | 395 | 0.4 | 75 | 63 | 4.7 | 3.8 | 1.6 | 42 | 56 | 9.9 | 1.6 | 0.5 | 150 | 120 | 0.4 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S4 | IEC | CPY04B6
FCU-210 | 20" | 43.25" | 10.5" | 605 | 0.4 | 75 | 63 | 21.9 | 20 | 2.4 | 42 | 56 | 4.8 | 22.6 | 0.9 | 150 | 120 | 1.3 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S4 | IEC | CPY08B6
FCU-211 | 20" | 43.25" | 10.5" | 605 | 0.4 | 75 | 63 | 21.9 | 20 | 2.4 | 42 | 56 | 4.8 | 22.6 | 0.9 | 150 | 120 | 1.3 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S4 | IEC | CPY08B6
FCU-212 | 20" | 31.25" | 10.5" | 395 | 0.4 | 75 | 63 | 4.9 | 4.1 | 1.6 | 42 | 56 | 9.9 | 1.8 | 0.5 | 150 | 120 | 0.4 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S4 | IEC | CPY04B6
FCU-215A | 24" | 75" | 14" | 1020 | 0.4 | 75 | 63 | 25.9 | 21.4 | 3.7 | 42 | 56 | 2.2 | 23.4 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CBY12B6
FCU-215B | 24" | 75" | 14" | 1020 | 0.4 | 75 | 63 | 25.9 | 21.4 | 3.7 | 42 | 56 | 2.2 | 23.4 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CBY12B6
FCU-215C | 24" | 75" | 14" | 1020 | 0.4 | 75 | 63 | 25.9 | 21.4 | 3.7 | 42 | 56 | 2.2 | 23.4 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CBY12B6
FCU-215D | 24" | 53" | 14" | 605 | 0.4 | 75 | 63 | 14.9 | 14.4 | 2.4 | 42 | 56 | 4.7 | 16.9 | 0.9 | 150 | 120 | 0.9 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CBY08B6
FCU-218 | 24" | 53" | 14" | 605 | 0.4 | 75 | 63 | 9.3 | 8.5 | 2.4 | 42 | 56 | 4.7 | 9.6 | 0.9 | 150 | 120 | 0.9 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CBY08B6
FCU-219 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 18.4 | 17.6 | 3 | 42 | 56 | 1.4 | 21.6 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-220 | 24" | 41" | 14" | 395 | 0.4 | 75 | 63 | 9.7 | 8.9 | 1.6 | 42 | 56 | 9.9 | 9.9 | 0.5 | 150 | 120 | 0.4 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CBY04B6
FCU-222 | 24" | 41" | 14" | 395 | 0.4 | 75 | 63 | 8.4 | 7.6 | 1.6 | 42 | 56 | 9.9 | 8.5 | 0.5 | 150 | 120 | 0.4 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CBY04B6
FCU-224 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 15.2 | 14.5 | 3 | 42 | 56 | 1.4 | 16.6 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-227 | 20" | 65.25" | 10.5" | 1020 | 0.4 | 75 | 63 | 26.6 | 24.8 | 3.7 | 42 | 56 | 2.2 | 25.5 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S4 | IEC | CPY12B6
FCU-228 | 20" | 43.25" | 10.5" | 605 | 0.4 | 75 | 63 | 15.8 | 12.9 | 2.4 | 42 | 56 | 4.8 | 11.6 | 0.9 | 150 | 120 | 1.3 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S3 | IEC | CPY08B6
FCU-229 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 18.6 | 17.7 | 3 | 42 | 56 | 1.4 | 19.1 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S4 | IEC | CPY10B6
FCU-230 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 20.6 | 16.9 | 3 | 42 | 56 | 1.4 | 12.7 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S3 | IEC | CPY10B6
FCU-231A | 20" | 65.25" | 10.5" | 1020 | 0.4 | 75 | 63 | 24.7 | 22.7 | 3.7 | 42 | 56 | 2.2 | 25 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY12B6
FCU-231B | 20" | 65.25" | 10.5" | 1020 | 0.4 | 75 | 63 | 24.7 | 22.7 | 3.7 | 42 | 56 | 2.2 | 25 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY12B6
FCU-C201A | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 21 | 17 | 3 | 42 | 56 | 1.4 | 13 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S4 | IEC | CPY10B6
FCU-C201B | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 21 | 17 | 3 | 42 | 56 | 1.4 | 13 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S4 | IEC | CPY10B6
FCU-C202 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 21 | 16.4 | 3 | 42 | 56 | 1.4 | 12.9 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S4 | IEC | CPY10B6
FCU-C203 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 21 | 16.4 | 3 | 42 | 56 | 1.4 | 12.9 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S4 | IEC | CPY10B6
FCU-C204 | 20" | 65.25" | 10.5" | 1020 | 0.4 | 75 | 63 | 21 | 16.4 | 3.7 | 42 | 56 | 2.2 | 12.9 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S4 | IEC | CPY12B6
FCU-C205 | 20" | 65.25" | 10.5" | 1020 | 0.4 | 75 | 63 | 32 | 26.5 | 3.7 | 42 | 56 | 2.2 | 26.4 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S4 | IEC | CPY12B6
FCU-D101 | 20" | 65.25" | 10.5" | 1020 | 0.4 | 75 | 63 | 21 | 20.1 | 3.7 | 42 | 56 | 2.2 | 23.5 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY12B6
FCU-D102 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 16.9 | 15.6 | 3 | 42 | 56 | 1.4 | 17.8 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D103 | 20" | 31.25" | 10.5" | 395 | 0.4 | 75 | 63 | 6.4 | 5.9 | 1.6 | 42 | 56 | 9.9 | 6.8 | 0.5 | 150 | 120 | 0.4 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY04B6
FCU-D104 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 16.9 | 15.6 | 3 | 42 | 56 | 1.4 | 17.8 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D105 | 20" | 43.25" | 10.5" | 605 | 0.4 | 75 | 63 | 12.5 | 11.4 | 2.4 | 42 | 56 | 4.8 | 13.3 | 0.9 | 150 | 120 | 1.3 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY08B6
FCU-D106 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 16.9 | 15.6 | 3 | 42 | 56 | 1.4 | 17.8 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D107 | 20" | 43.25" | 10.5" | 605 | 0.4 | 75 | 63 | 12.5 | 11.4 | 2.4 | 42 | 56 | 4.8 | 13.3 | 0.9 | 150 | 120 | 1.3 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY08B6
FCU-D108 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 16.9 | 15.6 | 3 | 42 | 56 | 1.4 | 17.8 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D109 | 20" | 43.25" | 10.5" | 605 | 0.4 | 75 | 63 | 12.5 | 11.4 | 2.4 | 42 | 56 | 4.8 | 13.3 | 0.9 | 150 | 120 | 1.3 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY08B6
FCU-D110 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 17.1 | 16.1 | 3 | 42 | 56 | 1.4 | 18.5 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D111 | 20" | 31.25" | 10.5" | 395 | 0.4 | 75 | 63 | 6.4 | 5.9 | 1.6 | 42 | 56 | 9.9 | 6.8 | 0.5 | 150 | 120 | 0.4 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY04B6
FCU-D113 | 20" | 65.25" | 10.5" | 1020 | 0.4 | 75 | 63 | 20.4 | 19.2 | 3.7 | 42 | 56 | 2.2 | 23.5 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY12B6
FCU-D201 | 20" | 65.25" | 10.5" | 1020 | 0.4 | 75 | 63 | 20.4 | 19.2 | 3.7 | 42 | 56 | 2.2 | 23.3 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY12B6
FCU-D202 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 16.6 | 15.3 | 3 | 42 | 56 | 1.4 | 16.3 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D203 | 20" | 31.25" | 10.5" | 395 | 0.4 | 75 | 63 | 8.7 | 7.9 | 1.6 | 42 | 56 | 9.9 | 8.1 | 0.5 | 150 | 120 | 0.4 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY04B6
FCU-D204 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 16.6 | 15.3 | 3 | 42 | 56 | 1.4 | 16.3 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D205 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 16.9 | 15.6 | 3 | 42 | 56 | 1.4 | 16 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D206 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 16.6 | 15.3 | 3 | 42 | 56 | 1.4 | 16.3 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D207 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 16.9 | 15.6 | 3 | 42 | 56 | 1.4 | 16 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D208 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 16.6 | 15.3 | 3 | 42 | 56 | 1.4 | 16.3 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D209 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 16.9 | 15.6 | 3 | 42 | 56 | 1.4 | 16 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D210 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 15.8 | 14.7 | 3 | 42 | 56 | 1.4 | 16.8 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D211 | 20" | 31.25" | 10.5" | 395 | 0.4 | 75 | 63 | 8.7 | 8.1 | 1.6 | 42 | 56 | 9.9 | 7.8 | 0.5 | 150 | 120 | 0.4 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY04B6
FCU-D213 | 20" | 65.25" | 10.5" | 1020 | 0.4 | 75 | 63 | 21.3 | 20 | 3.7 | 42 | 56 | 2.2 | 23.3 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY12B6
FCU-D301 | 20" | 65.25" | 10.5" | 1020 | 0.4 | 75 | 63 | 21.9 | 20.7 | 3.7 | 42 | 56 | 2.2 | 23.3 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY12B6
FCU-D302 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 17.4 | 16 | 3 | 42 | 56 | 1.4 | 16.3 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D303 | 20" | 31.25" | 10.5" | 395 | 0.4 | 75 | 63 | 9.1 | 8.4 | 1.6 | 42 | 56 | 9.9 | 8.1 | 0.5 | 150 | 120 | 0.4 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY04B6
FCU-D304 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 17.4 | 16 | 3 | 42 | 56 | 1.4 | 16.3 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D305 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 17.8 | 16.4 | 3 | 42 | 56 | 1.4 | 16 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D306 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 17.4 | 16 | 3 | 42 | 56 | 1.4 | 16.3 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D307 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 17.8 | 16.4 | 3 | 42 | 56 | 1.4 | 16 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D308 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 17.4 | 16 | 3 | 42 | 56 | 1.4 | 16.3 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D309 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 17.8 | 16.4 | 3 | 42 | 56 | 1.4 | 16 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D310 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 16.6 | 15.5 | 3 | 42 | 56 | 1.4 | 16.8 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-D311 | 20" | 31.25" | 10.5" | 395 | 0.4 | 75 | 63 | 9.1 | 8.4 | 1.6 | 42 | 56 | 9.9 | 8.1 | 0.5 | 150 | 120 | 0.4 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY04B6
FCU-D313 | 20" | 65.25" | 10.5" | 1020 | 0.4 | 75 | 63 | 22.3 | 21.1 | 3.7 | 42 | 56 | 2.2 | 23.3 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY12B6
FCU-ST114 | 24" | 75" | 14" | 875 | 0.4 | 75 | 63 | 19.1 | 18.4 | 3.7 | 42 | 56 | 2.2 | 22.8 | 1.7 | 150 | 120 | 3.2 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CBY10B6
FCU-ST116 | 24" | 75" | 14" | 1020 | 0.4 | 75 | 63 | 26.5 | 25.4 | 3.7 | 42 | 56 | 2.2 | 26.8 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CBY12B6
FCU-ST219 | 20" | 57.25" | 10.5" | 875 | 0.4 | 75 | 63 | 16.2 | 15.8 | 3 | 42 | 56 | 1.4 | 18.6 | 1.4 | 150 | 120 | 3.5 | 0.08 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY10B6
FCU-ST314 | 20" | 65.25" | 10.5" | 1020 | 0.4 | 75 | 63 | 16.5 | 16 | 3.7 | 42 | 56 | 2.2 | 19.9 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY12B6
FCU-ST316 | 20" | 65.25" | 10.5" | 1020 | 0.4 | 75 | 63 | 41.3 | 39.9 | 3.7 | 42 | 56 | 2.2 | 41.1 | 1.7 | 150 | 120 | 5.4 | 0.17 | 208 | 1 | MFR | NF | MFR | 2000 | S1 | IEC | CPY12B6
Expansion Tank Schedule
| Manufacturer | Model Number | Tank Volume | Lit | Max Accept. Factor | Tank Diameter |  | Tank Height |  |  | Shipping Weight |  | Max Operating Temp. | Max Working Pressure | System Connection | Finish | Water Circulator | Air Valve | Factory Precharge
Tag Name |  |  | GAL |  |  | In | mm | in | mm | IN | Lbs | Kg
Expansion Tank ET-1 | Amtrol | ST-30VC-DD | 16.5 | 63 | 0.68 | 15 | 381 | 25 | 636 | 0.75 | 48 | 22 | 200 | 150 PSIG | Stainless Steel | Red Oxide Primer | Turbulator | Schrader Valve w/ EPDM Seat | 55 PSIG
Back Flow Preventer Schedule
Tag name | Manufacturer | Model Number | Valve Size | Model Info
BFP-1 | Watts | 994- AGK-P Watts Air Gap | 4" | Non-rising stem resillient Seated gate valves
BFP-2 | Watts | SD-2 | 3/8" | SD-2 Watts 3/8 Carbonated Beverage Backflow Preventer
Circulating Pump Schedule
Tag Name | Manufacturer | Model Number | Pump Data |  |  |  |  | Conditions of Service |  |  |  | Motor Data
|  |  | Max operating Presure | Liquid Temp Range | Max Ambient Tempt | Flange Standard | Pipe Connection | Liquid | Temp | NPSH Required | Specific Gravity | P1 Max | Rated Voltage | Main Frequency | Enclosure Class | Insulation Class
CP-1 Circulating Pump | Grundfos | Magna3 40-180 FN | 12 bar | 110 °C | 40 °C | GF | GF 15/26/40/43 | Water | 60 °C | m | 0.985 | 600 W | 208 | 60 Hz | X4D | F
Wather Heater Schedule
Tag Name | Quantity | Manufacturer | Model | Power Source | Type of Unit | Orientation | Unit Capacity | BTUH Input | GPH | Electrical V
WH-1 | 3 | A.O. Smith | Cyclone | Gas Fired | Condensing | Vertical | 130 G | 600000 | 699 | 120V