- Verify proper voltage and phase

- Inspect condenser coil; clean as needed

- Check compressor contactors for wear.

- Measure and record amp draw on compressor and condenser fan motor; check against nameplate.

- Measure and record suction and head pressure

- Measure and record sub-cooling and super heat

- Verify proper operation of hot gas solenoid if applicable.

- Measure and record amp draw on evaporator fan motor.

- Clean condensate drain and check pipeline for clogging Advise whether drain pipe needs cleared.

- Check oil level and pressure

- Check refrigerant charge and moisture condition (via sightglass) and preform leak check

- Check lines for signs of wear.

- Lubricate motors and bearings if required.

- Check fan blades and motor mounting brackets for wear or missing parts (eg. Bolts and screws) and replace as needed.

- Clean condenser fans.

- Check economizer dampers and motors.

- Note time on defrost clock, is it running?  Compare to time above.

- Initiate defrost; measure and record amp draw of defrost.

- Check electrical connections and tighten as needed.

- Check electric wires in condensers and evaporator fans for signs of wear and repair as needed.

- Measure and record amp draw on drain pan heaters if applicable.

- Verify operation of hot gas defrost if applicable; verify defrost termination.

- Inspect and clean evaporator , including fans.

- Restart compressor after defrost termination.

- Verify proper operation of any low ambient controls if applicable.

- Clean area around equipment thoroughly.

- Note any needed repairs on service tickets.

Unit #1  	Middle  Hussman   Model #H1S00ESKX2001650   Serial #5035-0016

Unit #2		 Middle  Heat Craft   Model # BDT1500M6C  Serial #TL9L07933

Unit #3  	South  Heat Craft  Model #BDT1600M6C   Serial #T09L07932

Unit #4  	South  Hussman  Model # H15001SKX2110650  Serial # 5035-0015

Unit #5  	West  Hussman  Model # K0D150H2K  Serial # 611655-10B

Unit #6  	West  Hussman  Model #K0D150H2K  Serial # 611655-10D

Unit #7             	Hussman  Model # K0D150H2K  Serial # 611655-10C

Unit #8             	Hussman  Model # K0D150H2K  Serial #611655-10A

Unit #9  	Small Walk In Cooler    Copeland  #Model # CSAM-0100-1AC-0001

Unit #10 	Walk in Freezer    Hussman  Model # H300FSKX2110773 Serial # 2012-051-7